Contents

- Dry vs. Wet Contacts

- Dry vs Wet Contacts: A Safety-First Guide

- Dry vs. Wet Contacts (Controller Output Perspective)

- Dry Contact Actuators

- Dry vs. Wet Contacts

- Dry Contact Input Relays

- Dry Contact IoT Sensors

Use Ctrl + Click to open this Notion docs page

# Dry vs. Wet Contacts

1. Dry Contact (Potential Free Contact)

Definition: A contact that acts purely as a mechanical switch. It has no internal power source. It does not supply voltage or current.

Also Known As: Volt-Free Contact, Passive Switch.

The Physics: It is just two pieces of metal touching or separating. It provides a "Path" but not the "Traffic" (Electrons).

Isolation: The most important feature. The switch is electrically isolated from the device that controls it.

How to Read It: To know if a Dry Contact is Open or Closed, the reading device (like your Adeunis) must supply a tiny amount of voltage (called "Wetting Voltage") to see if the current can flow through.

Common Examples:

Relay contacts (Common/NO/NC).

Your Yellow Float Switch.

Your Magnetic Reed Switch.

Push buttons.

2. Wet Contact (Potential Contact)

Definition: A contact that provides its own voltage and current when it changes state.

Also Known As: Active Output, Powered Contact, Sourcing Output.

The Physics: It acts like a power outlet that turns on and off. When "On," it shoots electricity out.

No Isolation: The output shares the same power ground as the device itself.

Common Examples:

Transistor Outputs (PNP/NPN) on sensors.

A standard light switch (it sends 220V to the bulb).

PLC Digital Outputs (24V).

The Dragino SN50v3 5V Output (This is a Wet Output).

🏗️ Analysis for Vaculink 3.0 System

Now, let’s map this theory directly to your Adeunis ARF8170AR and Vaculink 3.0.

1. Your Sensors are "Dry"

The Float & The Magnet: These are Dry Contacts.

Why? They are passive. They have no battery inside. If you cut the wire and touched it to your tongue, you would feel nothing (0V).

Benefit for Sewer: Safety. You are not running live electricity into a wet, explosive sewer pit.

2. Your Adeunis Device is the "Wetting Source"

Since the sensors are dry, the Adeunis device must do the work.

The Process:

The Adeunis sends a tiny voltage (approx 3.6V from its battery) out on the Input Wire.

It waits to see if that voltage comes back on the Ground Wire.

If it comes back: The Dry Contact is Closed.

If it stops: The Dry Contact is Open.

3. The "Wet" Output Scenario (Future Proofing)

Adeunis Output Mode: The manual says the Adeunis can "drive relays."

How? If you configure a pin as an Output, the Adeunis turns that pin into a Wet Contact (Open Collector). It allows current to flow to ground.

Use Case: If you wanted Vaculink 3.0 to turn on a warning light at the pit, you would wire the light to the Adeunis output. The Adeunis would "sink" the current to turn the light on.

📊 Comparison Cheat Sheet (For your Technicians)

| Feature | Dry Contact (Your Sensors) | Wet Contact (Powered Devices) |
| --- | --- | --- |
| Power Source | None (Passive). | Internal (Active). |
| Voltage on Wire | 0V (until connected to a reader). | Always has Voltage (e.g., 5V, 24V, 220V). |
| Polarity | Doesn't matter (usually). | Critical (+/- matters). |
| Safety | High (Safe for water/gas). | Low (Risk of spark/short circuit). |
| Distance | Limited by wire resistance. | Limited by voltage drop. |
| Vaculink Example | Yellow Float, Magnet. | Dragino 5V Output. |

Teacher's Final Verdict for Vaculink 3.0

You have made the correct architectural choice by using Dry Contacts for the sewer monitoring.

Explosion Proof: Sewers have Methane gas. A Dry Contact (Reed Switch) is sealed and carries almost zero current, making it intrinsically safe (no sparks).

Universal: If a float breaks, you can buy any brand of float. As long as it has two wires and acts as a switch, it will work with the Adeunis. You are not locked into one sensor brand.

Battery Friendly: The Adeunis only "wets" the contact for a millisecond to check the status. This saves battery compared to powering a "Wet" sensor (like an ultrasonic) that needs constant power.

System Status:

Sensors: Dry (Passive).

Node: Adeunis (Active Reader).

Logic: Detect Open/Close of Dry Contact

→

→

Send LoRaWAN Packet.

# Dry vs Wet Contacts: A Safety-First Guide

Dry vs. Wet Contacts (Safety Focus)

1. The Core Distinction (The "Multimeter Test")

If you are unsure if a wire is Dry or Wet, use a Multimeter before connecting it to your IoT device.

Dry Contact (Safe):

Test: Put Multimeter probes on the two wires of the open switch.

Reading: 0 Volts.

Meaning: It is just a mechanical bridge. Safe to connect to Adeunis.

Wet Contact (Danger):

Test: Put Multimeter probes on the wires.

Reading: Voltage Present (e.g., 12V, 24V, 110V, 240V).

Meaning: It is carrying power. DO NOT CONNECT to Adeunis directly.

2. The "Fire Alarm" Analogy for Sewers

The video explains that Fire Alarm modules expect a "Clean" contact closure.

Your Adeunis ARF8170AR is the "Module".

It expects a "Clean" closure from the Float Switch.

The Risk: If a technician accidentally wires a 24V PLC output directly to the Adeunis input, the internal circuitry of the Adeunis will burn out immediately.

🏗️ Analysis for Vaculink 3.0 System

1. The "Wetting" Concept Clarified

The video mentions that Dry Contacts have "No Voltage." This is true until you connect them.

The Source: The Adeunis device itself provides the "Wetting Voltage" (approx 3.6V).

The Path: Adeunis Battery

→

→

White Wire

→

→

Float Switch

→

→

Green Wire

→

→

Adeunis Processor.

Conclusion: The Sensor must be Dry (Passive). The Node makes it Wet (Active) to read it.

2. Handling "Wet" Signals in the Field

Sometimes, you need to monitor a pump that is already powered.

Scenario: You want to know if the Vacuum Pump is running (240V).

Wrong Way: Connect 240V wires to Adeunis. (Explosion/Fire).

Right Way: Use an Interposing Relay.

Connect the 240V Pump wires to the Relay Coil.

Connect the Relay Contacts (NO) to the Adeunis.

Result: The Relay isolates the high voltage. The Adeunis sees a safe "Dry Contact" closure when the pump runs.

3. Safety in Hazardous Areas (ATEX/Methane)

Sewers contain Methane.

Wet Contacts: Arcing/Sparking is possible if the voltage/current is high (like the Fan example in the video). This is dangerous in a sewer.

Dry Contacts (via Adeunis): The Adeunis uses extremely low current (micro-amps). Even if the float switch sparks inside, the energy is too low to ignite methane. This is called Intrinsically Safe design principles.

📊 Implementation Checklist for Vaculink 3.0

Technician Training:

Rule #1: "Never connect a wire to the Adeunis box if that wire has voltage on it."

Rule #2: "Always measure the wires with a multimeter first. It must read 0 Volts."

Module Protection:

Unlike the "ET Modules" mentioned in the video which can accept voltage, your Adeunis Dry Contact version is strict. It only accepts potential-free switches.

The "Common" Terminal:

In the video, they mention "Common (COM)."

On your Adeunis, the Ground (GND) wire acts as the Common.

Input 1 and Input 2 both loop back to this Common Ground.

Dry vs. Wet Contacts (Controller Output Perspective)

1. The Controller's Dilemma

A controller (whether it's a Danfoss HVAC unit, an Omron PLC, or a Dragino Node) has to turn things on. It has two ways to do this:

A. Dry Contact Output (The "Switch")

Definition: The controller provides a relay closure, but NO Voltage.

Wiring Requirement: The installer must bring their own power source (External Loop).

Danfoss Example: Terminals 1 & 2.

Action: The controller closes the gate.

Power: Comes from the building's circuit breaker, goes through the contact, to the compressor.

Vaculink Analogy: This is like a standard Relay Output on a PLC. It can switch 24V DC or 230V AC because it is isolated.

B. Wet Contact Output (The "Source")

Definition: The controller shares its Own Internal Power to drive the load.

Wiring Requirement: Simpler. You just connect the load (Fan/Valve) directly to the terminal and Neutral/Ground.

Danfoss Example: Terminals 5 & 6.

Action: The controller sends its own 120V supply out to the Fan.

Vaculink Analogy: This is like the Dragino SN50v3 5V Output. It uses its own battery/power to drive the sensor.

🏗️ Analysis for Vaculink 3.0 System

How does this specific "HVAC" lesson apply to your "Sewer" architecture?

1. The "Hybrid" Nature of Controllers

The video highlights that the Danfoss controller has BOTH Dry and Wet terminals.

Your Omron PLC is the same.

Digital Outputs (Transistor/Source): These are Wet. They send 24V DC out to trigger the Contactor Coils.

Relay Outputs: These are Dry. You can use them to switch a completely different voltage (e.g., a 12V alarm siren) without frying the PLC.

2. Wiring the Dragino SN50v3 (Wet Output)

We previously discussed using the Dragino to power an Ultrasonic Sensor.

Concept: The Dragino 5V output is a Wet Contact.

Implication: You do not need an external battery for the Ultrasonic sensor. The Dragino "wets" the circuit.

Limit: You are limited by the Dragino's battery capacity (Amps). You cannot run a heavy motor, only a small sensor or a small relay coil.

3. Troubleshooting Vaculink Installations

When your technicians are in the field, they must know what they are measuring.

Scenario: Technician measures a PLC Output terminal to see if the pump should be running.

If it's a Wet Output: He puts one probe on the Terminal and one on Ground. He expects 24V.

If it's a Dry Output: He puts probes on both terminals of the relay. He checks for Continuity (Beep), not Voltage.

Danger: If he expects Voltage on a Dry Contact, he will think the PLC is broken when it reads 0V, even though the switch is closed.

📊 Quick Reference: Output Types

| Feature | Dry Output (Terminals 1-2) | Wet Output (Terminals 5-6) |
| --- | --- | --- |
| Power Source | External (You provide it). | Internal (Controller provides it). |
| Flexibility | High. Switch 12V, 24V, or 230V. | Low. Must match Controller Voltage. |
| Wiring | More wires (Loop in, Loop out). | Less wires (Direct to load). |
| Vaculink Use | Adeunis Input (Reading a switch). | PLC Output (Driving a Contactor). |

Teacher's Summary

Dry = Flexibility. You choose the voltage.

Wet = Simplicity. The voltage is ready to go.

The Golden Rule: Never connect an external power source to a Wet Output. You will cause a short circuit (The Controller's Power vs. Your External Power = Boom).

# Dry Contact Actuators

1. What is a Dry Contact Actuator?

Definition: A smart relay or switch where the output terminals are electrically isolated from the device's own power supply.

The Output: It provides NO Voltage. It acts purely as a mechanical bridge.

Terminals:

COM (Common): The signal entry point.

NO (Normally Open): The circuit closes (connects to COM) when the device is active.

NC (Normally Closed): The circuit opens (disconnects from COM) when the device is active.

Why use it?

Voltage Independence: You can power the smart switch with 120V AC, but use the relay to close a 12V DC circuit or a 24V AC circuit.

Safety: It prevents "Back-feeding" voltage into sensitive control boards (like garage door openers or boiler thermostats).

2. Control Logic: Latching vs. Inching

Smart relays generally offer two distinct modes of operation to match the equipment they are controlling.

A. Edge Mode (Latching / Maintained)

Behavior: When you send an "ON" command, the relay closes and stays closed until you send an "OFF" command.

Analogy: A standard light switch.

Use Case: Controlling continuous loads like a floodlight, a heater, or a fan.

B. Pulse Mode (Inching / Momentary)

Behavior: When you send an "ON" command, the relay closes for a specific duration (e.g., 0.5 seconds) and then automatically opens again.

Analogy: A doorbell button or a computer power button.

Use Case:

Toggling: Many industrial controllers and garage doors use a single input pin to toggle states (Open

→

→

Stop

→

→

Close). They expect a short pulse, not a continuous signal.

Resetting: Briefly cutting power to reboot a frozen device.

3. The "Decoupled" (Detached) Relay

Concept: Separating the physical switch input from the relay output within the same device.

Standard Mode: Pressing the button physically triggers the relay.

Detached Mode: Pressing the button sends a signal to the Cloud/Controller, but does not trigger the relay. The Controller decides if/when to trigger the relay based on software logic.

Benefit: Allows for complex automation rules (e.g., "Only trigger the relay if the button is pressed AND it is after 6:00 PM").

4. The "Open Loop" Risk (Feedback Gap)

A major limitation of simple dry contact actuators is the lack of state verification.

The Problem: The device knows it clicked the relay to "Open" the gate. However, it does not know if the gate actually opened (the motor might be broken, or the path blocked).

The Solution (Closed Loop): In high-reliability systems, you cannot rely on the actuator alone. You must install a separate Sensor (e.g., a magnetic contact) to confirm the physical position of the equipment and report it back to the control system.

Summary

Dry Contact Outputs are the universal adapter of the automation world. They allow modern IoT devices to control legacy equipment safely.

Inching (Pulse) Logic is essential for interacting with digital controllers that expect momentary button presses.

Input/Output Isolation is the key feature that distinguishes professional-grade switching from basic smart plugs.

# Dry vs. Wet Contacts

1. Dry Contact (Potential Free)

Definition: A contact that does not carry or supply its own voltage or current. It acts purely as a passive switch.

Synonyms: Voltage-Free Contact, Potential-Free Contact, Zero-Volt Contact.

Operating Principle:

It functions like a mechanical gate.

Its only job is to Open (break) or Close (make) a circuit path.

The power source must be supplied by the external circuit that is being controlled.

Key Characteristic: Isolation. Because it has no internal power, it electrically isolates the control device from the load circuit.

Typical Use Cases:

Switches connecting to PLC inputs.

Thermostat control signals.

Alarm relay outputs.

2. Wet Contact (Potential)

Definition: A contact that carries its own voltage and current. When the contact closes, it delivers power directly to the load.

Synonyms: Powered Contact, Active Output, Sourcing Output.

Operating Principle:

It acts as a power source.

The power is "intrinsic" to the device controlling the contact.

When switched ON, the contact doesn't just complete a path; it sends voltage (e.g., 24V, 120V) down the wire.

Key Characteristic: Integrated Power. Wiring is simpler because you don't need an external loop supply, but you lose electrical isolation.

Typical Use Cases:

Solid-state sensors powering a light or buzzer.

Thermostat terminals controlling a fan (R to G).

Controller outputs driving a solenoid valve directly.

3. The Core Analogies

These analogies help visualize the flow of energy:

Dry Contact = The Drawbridge Operator.

The operator (the switch) controls the bridge.

The operator does not carry the cars (the current).

The cars (current) come from an external road (circuit).

Wet Contact = The Road Bridge.

The bridge itself supports and carries the traffic (current).

If the bridge connects, traffic flows immediately because the bridge is part of the highway system.

4. Summary Comparison

| Feature | Dry Contact | Wet Contact |
| --- | --- | --- |
| Voltage Source | External. Must be supplied by the receiving device. | Internal. Supplied by the switching device itself. |
| Current Flow | None until connected to an external loop. | Flows immediately upon closure to the load. |
| Primary Role | Control / Signaling. (Logic). | Power Switching. (Action). |
| Safety | High (Isolated). | Lower (Risk of voltage mismatch/short). |

Engineering Takeaway

Use Dry Contacts when you need to interface two different systems (e.g., a Fire Alarm talking to an Elevator) to ensure their voltages don't clash.

Use Wet Contacts when you want to drive a device directly (e.g., a Motion Sensor turning on a Floodlight) to simplify wiring.

# Dry Contact Input Relays

1. Definition & Functionality

What is it? A specialized relay designed to be triggered by a simple mechanical switch closure (a "dry contact") without requiring an external power source for the trigger loop.

How it works:

The relay unit itself generates an internal low-voltage signal (typically Class 2, ~24 VDC).

This voltage is sent out via the input wires (often White/Yellow or similar low-voltage leads).

When the external dry contact (e.g., a thermostat, reed switch, or push button) closes, it completes the circuit, allowing the micro-amp current to flow back to the relay.

The internal electronics detect this flow and energize the high-voltage coil to switch the load.

2. Key Engineering Advantages

Self-Wetting: The relay provides the "wetting voltage" for the switch. The installer does not need to find a separate 24V transformer to power the control loop.

Wiring Efficiency:

Because the control signal is Class 2 Low Voltage and very low current (micro-amps), it generally does not require conduit (depending on local codes).

Installers can use inexpensive cabling like CAT5 or standard thermostat wire.

Long Distance: The control signal can travel thousands of feet without significant voltage drop issues, unlike standard 24V AC relay coils.

Safety & Isolation: There is complete galvanic isolation between the low-voltage control input (the switch) and the high-voltage load (120V/277V). This protects the switching device (e.g., a delicate BAS controller) from high-voltage spikes.

3. Common Applications

Building Automation Systems (BAS): Interfacing a BAS controller's low-current dry contact output to switch heavy loads like motors or lighting banks.

Interlocking Loads: Using a Current Sensor on Load A to close a dry contact, which triggers the Dry Contact Input Relay to turn on Load B (e.g., turning on a booster fan when a dryer runs).

Door/Window Status: Using magnetic reed switches (security sensors) to directly control lighting or air curtains. When the door opens, the reed switch closes, triggering the relay.

Safety Cut-offs: "Appliance Garage" applications where power to an outlet must be cut when a cabinet door is closed.

4. Advanced Variations

Time Delay Logic: Some models integrate timing logic directly into the relay.

Delay on Make (DOM): Wait X seconds after the switch closes before turning on the load (prevents short-cycling).

Delay on Break (DOB): Keep the load running for X seconds after the switch opens (e.g., keeping an exhaust fan running for 5 minutes after the light is turned off).

Override Switches: Integrated "Hand-Off-Auto" (HOA) switches allow technicians to manually force the relay on or off for testing, bypassing the dry contact input.

5. Housing & Enclosures

NEMA 1: Standard indoor metal or plastic housing.

NEMA 4X: Weather-tight housing for outdoor or wash-down environments.

Track Mount: Designed for installation inside control panels (DIN rail or snap-track).

Summary

Dry Contact Input Relays simplify installation by combining the power supply, isolation logic, and switching mechanism into one box.

They are the ideal solution when you need to control a high-voltage device using a passive, unpowered switch over a long distance.

# Dry Contact IoT Sensors

1. Technical Definition: The "Potential-Free" Interface

A Dry Contact (also known as a "Volt-Free" or "Potential-Free" contact) is an electrical circuit where the device being monitored provides no voltage or current to the sensor.

The Sensor's Role: It acts as a passive observer that detects whether a circuit is physically bridged (Closed) or disconnected (Open).

The Logic: It is purely binary. It translates a mechanical state into a digital signal (0 or 1).

2. Operational Principle

The sensor monitors the continuity of a loop.

Open State: The circuit is interrupted. This typically signals a "Resting" state (e.g., a door is closed, an alarm is inactive, or a machine is off).

Closed State: The circuit is completed. This signals an "Event" has occurred (e.g., a hatch has opened, a float has lifted, or a limit switch has been hit).

3. Core Engineering Advantages

A. Extreme Energy Efficiency

Because the monitored circuit does not emit current, the sensor only uses power to detect the state change and transmit the radio packet.

Autonomy: This passive operation allows battery life to extend from 5 to 15+ years, depending on the transmission frequency.

Remote Suitability: Ideal for "install and forget" deployments in hard-to-reach areas where frequent maintenance is impossible.

B. Industrial Robustness

Electrical Safety: The absence of voltage at the contact point reduces the risk of electrical wear, arcing, or short-circuiting.

EMI Immunity: Because there is no active current in the loop, the system is highly resistant to electromagnetic interference (EMI), ensuring accurate readings in noisy industrial environments.

Environmental Protection: High-quality units are typically IP68 rated, meaning they are dust-tight and can survive prolonged submersion in water.

Thermal Range: Designed to operate in extreme temperatures, from frozen storage to high-heat industrial zones.

C. Simplified Integration

No Calibration: Unlike analog sensors (which measure pressure or temperature scales), dry contacts require no calibration or complex setup.

Protocol Compatibility: These devices are typically "Plug-and-Play" with major LPWAN (Low Power Wide Area Network) protocols like LoRaWAN and Sigfox.

4. Categorized Use Cases

| Sector | Application | Engineering Goal |
| --- | --- | --- |
| Industrial | Valve/Hatch monitoring | Ensure safety and prevent unauthorized access. |
| Industrial | Conveyor Limit Switches | Detect mechanical travel limits to prevent equipment damage. |
| Smart Building | Occupancy-Based HVAC | Detect room usage to automate lighting and heating (Energy Sobriety). |
| Smart Building | Security & Access | Real-time monitoring of emergency doors, windows, and technical rooms. |
| Healthcare | Equipment Health | Monitoring the status of emergency gear (e.g., Defibrillators) for malfunctions. |
| Infrastructure | Network Integrity | Detecting tampering or incidents on water/gas valves and electrical cabinets. |

5. Advanced Versatility: Associative Sensing

While the sensor itself is binary, it can be used as a Communication Bridge for other "dumb" mechanical sensors. By connecting a mechanical level-float, a vibration-switch, or a thermal-switch to the dry contact input, you transform a simple mechanical device into a connected IoT asset.

6. Fleet Management & Maintenance

Professional deployments utilize specialized platforms (such as Adeunis KARE) to manage these sensors.

Configuration: Remote adjustment of transmission intervals (periodic vs. event-triggered).

Monitoring: Real-time tracking of battery levels and signal strength (RSSI/SNR).

Decoding: Translating raw binary "telegrams" into actionable business data.

Summary

Dry Contact IoT sensors are the "sentinels" of the connected world. They prioritize reliability, longevity, and simplicity over high-speed data. In any environment where you need to know if a state is "A" or "B" without running power cables, a Dry Contact sensor is the standard engineering solution.