Contents

- Configurable Inputs & Alert Logic

- Distributed I/O & RS-485 Integration

- Centralized Building Management

- Energy Sobriety & Occupant Comfort

- Wireless I/O Acquisition Modules

Use Ctrl + Click to open this Notion docs page

# Configurable Inputs & Alert Logic

1. The "Generic Input" Architecture

Concept: Designing hardware with generic, multipurpose input terminals (often labeled Aux, S1/S2, or Digital In) rather than function-specific terminals (like Fire or Leak).

Software Mapping: The specific function of the terminal is assigned via the system's software configuration menu.

Example: A single hardware input can be configured to act as a "Water Leak Sensor," a "Dirty Filter Monitor," or a "System Shutdown Trigger" depending on what is installed.

Engineering Benefit: Reduces manufacturing complexity (one SKU covers many use cases) and increases flexibility for the installer in the field.

2. Software-Defined Polarity (NO/NC)

The Problem: Field sensors vary in logic. Some are Normally Open (NO) (close on alarm), while others are Normally Closed (NC) (open on alarm for fail-safety).

The Solution: Instead of requiring physical relays or specific sensor types, modern controllers include a software toggle to invert the logic state.

Setting NO: Circuit Close = Alarm.

Setting NC: Circuit Open = Alarm.

Benefit: Allows the integration of a wide ecosystem of third-party sensors without hardware compatibility issues.

3. Actionable HMI (Human Machine Interface)

Principle: An alarm system should not just report what is wrong; it should facilitate the resolution.

Closing the Loop: Advanced HMIs display not only the error message (e.g., "Unit Failure") but also dynamic contact information (e.g., "Call Technician at 555-0199").

Value: This reduces the "Time to Resolution" by providing the end-user with immediate next steps, rather than forcing them to search for manuals or support numbers during an emergency.

4. Usage-Based vs. State-Based Alerts

State-Based: Triggers immediately when a switch changes position (e.g., Water Leak).

Usage-Based: Triggers based on accumulated data or time (e.g., "Change Filter" after 500 hours of runtime).

Implementation: The controller tracks the duration of specific inputs (e.g., Fan Run Signal) to generate predictive maintenance alerts before a hard failure occurs.

Summary

Hardware provides the connection; Software provides the context.

Flexibility: A robust control system allows the installer to define Input Type (Function) and Input Logic (Polarity) through the interface.

User Experience: The most effective monitoring systems bridge the gap between Detection (The Sensor) and Action (The Service Call).

# Distributed I/O & RS-485 Integration

1. The Concept of Distributed I/O

Definition: Instead of running every single sensor wire back to a massive central controller (Star Topology), you place small input/output modules locally (e.g., inside a wall switch box) and connect them via a single communication bus.

Benefits:

Drastic Cabling Reduction: You only run a 4-core cable (Power + Data) between rooms, rather than dozens of individual copper wires.

Scalability: You can add more modules to the bus without changing the central controller hardware.

Retrofit Friendly: Ideal for upgrading existing buildings where pulling new bundles of wire is impossible.

2. Communication Protocol: RS-485

The module uses RS-485 (TIA-485) as its physical transport layer. This is the industry standard for wired automation.

Long Distance: Supports cable runs up to 1,200 meters (4,000 ft), far exceeding Wi-Fi or Ethernet limits.

Noise Immunity: Uses Differential Signaling (Data+ and Data-). If electrical noise hits the cable, it affects both wires equally, so the difference between them remains the same, preserving the data.

Topology: Daisy-chain (Linear) topology. Modules are connected in a series.

Wiring: Typically requires 2 wires for data (A/B) and 2 wires for power (V+/GND).

3. Input Logic Configuration (Software Defined)

A key engineering feature of modern I/O modules is the ability to define how a physical input is interpreted via software.

Rising Edge: Trigger an event only when the contact closes (Button Pressed).

Falling Edge: Trigger an event only when the contact opens (Button Released).

Toggle/Change of State: Trigger an event whenever the state changes (Standard Light Switch behavior).

Application: This allows a single hardware module to interface with:

Momentary Pushbuttons (Doorbell style).

Latching Rocker Switches (Traditional light switches).

Sensors (Magnetic contacts, Smoke detectors).

4. Power Considerations (Voltage Drop)

When running DC power over long distances (like the 300m test mentioned), engineers must calculate Voltage Drop.

The Physics: Copper wire has resistance. Over 300m, a 12V source might arrive as 11V or 10V at the load.

Design Rule:

Use 24V DC for long runs instead of 12V or 5V. Higher voltage results in lower current for the same power, reducing voltage drop.

Ensure the I/O module has a wide input voltage range (e.g., 9V–30V) to tolerate these drops without resetting.

5. Bridging "Legacy" to "Smart"

This type of hardware serves as a Bridge.

Legacy Side: Connects to "Dumb" dry contacts (old switches, reed relays).

Smart Side: Connects to a central controller (Home Assistant, PLC, SCADA) via RS-485.

Result: It digitizes the state of mechanical devices, allowing them to participate in complex automation logic without replacing the mechanical devices themselves.

Summary

RS-485 is the preferred choice for wired, long-distance, reliable building automation.

Distributed I/O minimizes wiring complexity.

Software-defined Inputs allow universal compatibility with various switch types.

# Distributed I/O & RS-485 Integration

1. The Concept of Distributed I/O

Definition: Instead of running every single sensor wire back to a massive central controller (Star Topology), you place small input/output modules locally (e.g., inside a wall switch box) and connect them via a single communication bus.

Benefits:

Drastic Cabling Reduction: You only run a 4-core cable (Power + Data) between rooms, rather than dozens of individual copper wires.

Scalability: You can add more modules to the bus without changing the central controller hardware.

Retrofit Friendly: Ideal for upgrading existing buildings where pulling new bundles of wire is impossible.

2. Communication Protocol: RS-485

The module uses RS-485 (TIA-485) as its physical transport layer. This is the industry standard for wired automation.

Long Distance: Supports cable runs up to 1,200 meters (4,000 ft), far exceeding Wi-Fi or Ethernet limits.

Noise Immunity: Uses Differential Signaling (Data+ and Data-). If electrical noise hits the cable, it affects both wires equally, so the difference between them remains the same, preserving the data.

Topology: Daisy-chain (Linear) topology. Modules are connected in a series.

Wiring: Typically requires 2 wires for data (A/B) and 2 wires for power (V+/GND).

3. Input Logic Configuration (Software Defined)

A key engineering feature of modern I/O modules is the ability to define how a physical input is interpreted via software.

Rising Edge: Trigger an event only when the contact closes (Button Pressed).

Falling Edge: Trigger an event only when the contact opens (Button Released).

Toggle/Change of State: Trigger an event whenever the state changes (Standard Light Switch behavior).

Application: This allows a single hardware module to interface with:

Momentary Pushbuttons (Doorbell style).

Latching Rocker Switches (Traditional light switches).

Sensors (Magnetic contacts, Smoke detectors).

4. Power Considerations (Voltage Drop)

When running DC power over long distances (like the 300m test mentioned), engineers must calculate Voltage Drop.

The Physics: Copper wire has resistance. Over 300m, a 12V source might arrive as 11V or 10V at the load.

Design Rule:

Use 24V DC for long runs instead of 12V or 5V. Higher voltage results in lower current for the same power, reducing voltage drop.

Ensure the I/O module has a wide input voltage range (e.g., 9V–30V) to tolerate these drops without resetting.

5. Bridging "Legacy" to "Smart"

This type of hardware serves as a Bridge.

Legacy Side: Connects to "Dumb" dry contacts (old switches, reed relays).

Smart Side: Connects to a central controller (Home Assistant, PLC, SCADA) via RS-485.

Result: It digitizes the state of mechanical devices, allowing them to participate in complex automation logic without replacing the mechanical devices themselves.

Summary

RS-485 is the preferred choice for wired, long-distance, reliable building automation.

Distributed I/O minimizes wiring complexity.

Software-defined Inputs allow universal compatibility with various switch types.

# Centralized Building Management

1. Digital Transformation vs. Physical Renovation

In the building sector, there are two ways to save energy:

Energy Renovation: Replacing windows, adding insulation, or installing new boilers. (Expensive, slow, high CAPEX).

Digital Transformation: Adding a "Smart Layer" (Sensors + Software) to existing equipment to optimize how they run. (Cheaper, fast, high ROI).

Engineering Goal: Achieve ~15% energy savings just by using data to run existing machines more intelligently.

2. The "Programmable Building" Concept

Traditional Building Management Systems (BMS) are often static—they have a fixed schedule (e.g., "Lights on at 8 AM"). A "Programmable Building" uses Real-Time Logic:

Event-Driven: "If a window is open, turn off the heater in that room immediately."

Usage-Driven: "If the CO2 level is low, reduce the fan speed to save electricity."

Predictive-Driven: "If the weather forecast says it will be sunny at noon, don't turn the boiler on full power this morning; wait for the sun to heat the building."

3. LoRaWAN Device Classes (A vs. C)

When using a device like the Adeunis Dry Contact for Control, you must choose the correct LoRaWAN Class. This is a fundamental architectural decision.

| Feature | Class A (Autonomous) | Class C (Continuous) |
| --- | --- | --- |
| Power Source | Battery (10-20 years life). | External Power (Mains/DC). |
| Communication | Device sleeps; only wakes up to send data. | Device is always listening for commands. |
| Latency | High. You can only send a command after the device wakes up to send an uplink. | Low. You can send a command at any time; the device reacts instantly. |
| Use Case | Monitoring (Open/Close sensors). | Actuation (Turning on lights, resetting a PLC). |

4. The "Mini-PLC" Actuator

The webinar describes the Dry Contact device as a "Mini-PLC."

Input Side: Detects a state (e.g., a "Fault" signal from a pump).

Output Side: Contains a Relay. It can physically "click" to bridge a circuit.

Interfacing: Because it is a Dry Contact, it can be wired into the "External Trigger" port of almost any machine (Boilers, AC Units, Gate Controllers) without worrying about voltage mismatches.

5. Low-Code Logic (Block-Based Programming)

Modern IoT platforms are moving toward "Block-Based" logic (similar to the Scratch language).

The Benefit: It allows Facility Managers (who are not software engineers) to create complex rules.

Logic Example: [IF] Presence is False [AND] Time is > 7 PM [THEN] Set Relay to OPEN (Turn off lights).

📊 Summary Table: Energy Optimization Use Cases

| Use Case | Input Sensor | Logic / Algorithm | Output Action |
| --- | --- | --- | --- |
| HVAC Control | Temp / Occupancy | Predictive (Weather) | Adjust Setpoint |
| Lighting | Motion / Light level | Event-based | Toggle Relay |
| Load Shedding | Energy Meter | Tariff-based (Peak/Off-peak) | Cut non-essential power |
| Autoconsumption | Solar Forecast | Predictive | Pre-heat water during sun peaks |
| Leak Detection | Water Meter (Pulse) | Anomaly Detection | Close Master Valve |

Summary

Centralized Management is about moving the "Brain" of the building from individual thermostats to a single Cloud Platform.

Class C LoRaWAN is the standard for real-time remote control.

Interoperability is key: The software must be able to read data from one brand of sensor (Adeunis) and send a command to another brand of machine (e.g., a Daikin AC unit).

# Energy Sobriety & Occupant Comfort

1. The Strategy: Energy Sobriety (Sobriété Énergétique)

Definition: The practice of reducing energy consumption through behavioral changes, optimized building management, and technical fine-tuning, rather than large-scale structural renovation.

The Balancing Act: The primary engineering challenge is to reduce energy waste (Sobriety) without degrading the well-being of the inhabitants (Comfort).

Key Drivers: Regulatory mandates (e.g., Decret Tertiaire/BX in France) requiring buildings over a certain size/consumption threshold to implement automated controls and reporting.

2. The Hardware Layer: IoT Sensors

Protocol Diversity: Industrial IoT uses a mix of protocols based on the environment:

LoRaWAN/Sigfox: For long-range, deep indoor penetration, and battery efficiency.

WMBus: For local utility sub-metering.

Performance Metrics:

Battery Life: Target >10 years to minimize maintenance labor costs.

Emissions: IoT sensors are "Electromagnetically Quiet," typically emitting ~25mW (compared to 2000mW for a 4G phone), making them safe for continuous indoor occupancy.

Deployment Density: A standard design guideline for Indoor Air Quality (CO2) is 1 sensor per 500 m² or 1 sensor per high-occupancy room.

3. The Integration Layer: Multiprotocol Gateways

The Hub Concept: A centralized "concentrator" or gateway is required to bridge disparate systems.

Interoperability: The gateway must speak both "Modern IoT" (LoRaWAN) and "Legacy Building" protocols (BACnet, Modbus, KNX, M-Bus).

Bidirectional Control: Professional gateways allow for both Data Acquisition (Reading sensors) and Command Execution (Adjusting setpoints or toggling relays).

Coverage: In urban environments, a single high-quality gateway typically covers a 700–800m radius, sufficient for multi-floor monitoring in dense buildings.

4. Data Analytics: "Time in Comfort Zone" (TICZ)

Beyond Averages: Engineers should avoid using simple temperature averages, which can hide extremes (e.g., a room that is freezing at night and boiling during the day might have a "perfect" 20°C average).

The TICZ Indicator: Tracks the exact duration (percentage of time) a room stays within predefined comfort thresholds (e.g., 19°C–21°C).

Actionable Insights: Heatmaps correlating temperature, sunlight, and occupancy help identify "Energy Leaks" (e.g., heating a room that remains warm due to natural sunlight).

5. Economic & Regulatory ROI

| Metric | IoT / Digital Optimization | Physical Renovation |
| --- | --- | --- |
| Typical Energy Savings | ~20% | 15% - 20% |
| Return on Investment (ROI) | < 2 Years | > 15 Years |
| Complexity | Low (Wireless, no cabling) | High (Structural work) |

6. Project Management Best Practices

Phase 1: Strategy. Define essential parameters. Avoid "Data Overload" by only measuring what you intend to act upon.

Phase 2: Site Survey. Perform radio mapping to ensure the gateway can "hear" sensors in difficult areas like basements or boiler rooms.

Phase 3: Continuous Improvement. Energy sobriety is a cycle, not a one-time setup. Use anomaly detection to find sensors that have drifted or fallen offline.

Summary

Digitalization is the fastest path to regulatory compliance and energy reduction.

Hybrid Networks (mixing public and private LoRa) provide the best balance of coverage and data control.

Occupant Engagement is critical; data should be used to prove to occupants that sobriety measures are maintaining their comfort, not reducing it.

# Wireless I/O Acquisition Modules

1. Device Concept & Positioning

Definition: A wireless edge device designed to interface directly with sensors (Input/Output) and transmit data over standard wireless networks (WiFi/WLAN) without requiring a physical PLC or heavy cabling.

Target Environment: Industrial 4.0 applications, legacy machine retrofitting, and remote environmental monitoring.

The "IAPP" Functional Logic:

I (Input/Acquisition): Reads raw data from sensors (Digital Dry/Wet contacts, Analog Current/Voltage).

P (Processing): Performs edge computing tasks like scaling, averaging, filtering, and unit conversion before transmitting.

P (Publishing): Pushes processed data to a cloud server, SCADA, or acts as a local web server.

2. Hardware Architecture

Input Types:

Digital: Supports both Dry Contact (unpowered switches) and Wet Contact (powered signals).

Analog: Configurable for Voltage (0-10V) or Current (4-20mA).

Counters: High-speed counters (up to 3 kHz) with 32-bit storage for metering applications.

Power Requirements:

Industrial Standard: 10–30V DC input (compatible with standard control panel power supplies).

Developer Options: Micro-B USB power (5V) for bench testing and configuration.

Connectivity Hardware:

Frequency: 2.4 GHz (IEEE 802.11 b/g/n).

Antenna: Reverse SMA connector (allows swapping for high-gain antennas if the signal is weak). Default gain is usually ~3.6 dBi.

3. Network Operation Modes

Understanding the topology is critical for deployment.

Mode  Description     Max Connections       Use Case

AP Mode (Access Point)         The module broadcasts its own WiFi network (SSID).            1 Client           Initial Configuration. A technician connects a laptop directly to the module to set IP/Parameters.

Infrastructure Mode   The module acts as a client and connects to an existing Factory WiFi Router.    Multiple (3-4)  Normal Operation. The module sits on the LAN and talks to the Server/SCADA.

4. Communication Protocols

These modules bridge the gap between OT (Operational Technology) and IT (Information Technology).

A. Industrial Protocols (OT)

Modbus TCP: The module acts as a Slave. Standard for communicating with PLCs and SCADA systems.

Modbus RTU: (Specific models only) The module acts as a Master, collecting data from other RS-485 slave devices and sending it over WiFi.

B. IT/IoT Protocols

RESTful API: Uses standard HTTP methods (GET, POST). Allows web developers to read sensor data using simple JSON requests.

MQTT: A lightweight, publish-subscribe protocol. Ideal for cloud integration (AWS, Azure) because it pushes data out rather than waiting to be polled, saving bandwidth.

5. Data Integrity & Security (The "Data Logger")

A critical feature for wireless devices is handling network dropouts.

Internal Buffering: The module contains onboard memory (e.g., 10,000 samples).

RTC (Real Time Clock): Battery-backed clock ensures every data point is timestamped accurately, even if power/network is lost.

Recovery Logic:

Network Lost

→

→

Store data in internal memory.

Network Restored

→

→

Batch upload historical data to fill the gap in the database.

Security Layers:

Transport: HTTPS / TLS / SSL (Encrypted transmission).

Network: WPA2 Enterprise / EAP (WiFi security).

Access: User Authentication for web configuration.

6. Application Scenarios

Machine Monitoring (OEE): Counting cycles on mechanical punch presses without installing a full PLC.

Environmental Monitoring: Tracking temperature/humidity in Data Centers or Greenhouses (Plants Factories).

Smart Infrastructure: Parking lot sensor monitoring and LED guidance control.

Cold Chain: Monitoring commercial refrigerators to prevent spoilage (predictive maintenance).

Summary

Wireless I/O Modules replace the "Cable Run" with a "Data Stream."

Edge Processing reduces server load by filtering data at the source.

Protocol Flexibility (Modbus + MQTT) allows these devices to speak to both old PLCs and modern Cloud Dashboards simultaneously.