Contents

- IoT Ecosystem Architecture

- IoT for Technical Performance

- IoT Sensor Deployment & Installation

- IoT Transport Protocols

Use Ctrl + Click to open this Notion docs page

# IoT Ecosystem Architecture

1. The Three Pillars of a Complete Solution

Successful large-scale IoT projects (like social housing) typically require an ecosystem of three distinct technical partners working in synergy:

Device Manufacturer (The Hardware): Responsible for the physical sensors (e.g., Adeunis). Focuses on metrology, battery life, and protocol compliance.

Network Operator (The Connectivity): Responsible for the transport layer (e.g., Requea). Manages the LoRaWAN gateways, the LoRa Network Server (LNS), and ensures packet delivery.

Hypervision Platform (The Intelligence): Responsible for data visualization and business logic (e.g., Citron). Aggregates data from multiple sites into actionable dashboards for the end-user.

2. Sensor Classifications & Use Cases

In building management, sensors are generally categorized into three functional domains:

A. Energy Performance

Pulse Counters: Battery-operated devices (often ATEX certified) that count pulses from existing water, gas, or electricity meters.

Modbus Interfaces: Connect to larger energy meters or sub-metering systems to read complex registers.

TIC (Télé-Information Client): Specific to regions like France, these read data directly from the port of smart electricity meters (e.g., Linky).

B. Technical Performance (Maintenance)

Dry Contact Interfaces: Monitor binary states of critical equipment (Elevator faults, Smoke vent positions, Door security).

Temperature Probes (Contact/Immersion): Monitor Domestic Hot Water (DHW) loops to ensure temperatures remain high enough to prevent Legionella bacteria growth but low enough to save energy.

C. Comfort (Indoor Air Quality)

IAQ Sensors: Measure Temperature, Humidity, CO2, and VOCs (Volatile Organic Compounds).

Goal: Ensure tenant well-being and prevent "Sick Building Syndrome" by monitoring ventilation effectiveness.

3. Network Topology & Constraints (LoRaWAN)

Star Topology: LoRaWAN utilizes a "Star-of-Stars" topology. Sensors communicate directly with Gateways. They do not mesh or relay data to each other.

Deep Penetration: The modulation is specifically chosen for its ability to penetrate concrete basements and boiler rooms where technical meters are located.

Battery Life Physics: Autonomy (up to 15 years) is heavily dependent on the Spreading Factor (SF).

Engineering Rule: Sensors in poor coverage areas automatically increase their SF to be heard, which increases transmission time and drains the battery significantly faster. Good network planning is essential for battery longevity.

4. The Role of the Hypervision Platform

The value of IoT is not in the data collection, but in the operational response. A robust platform provides:

Multi-Site Aggregation: Viewing thousands of buildings on a single map.

Automated Ticketing: Converting a "Leak Alarm" directly into a work order for a maintenance contractor.

Comfort Analysis: Tracking the percentage of time a room spends outside of defined comfort zones (e.g., "Too Cold" duration).

5. Deployment Strategy: The Two-Step Process

To avoid project failure, deployment follows a strict engineering sequence:

Theoretical Coverage Study: Using software simulations to estimate how many gateways are needed based on building geometry and materials.

On-Site Radio Mapping: Using a Field Test Device (FTD) to physically validate signal strength at sensor installation points. This confirms gateway placement and validates the battery life calculations.

Summary

Integration is Key: No single company usually does it all. The interface between the Sensor, the LNS, and the Dashboard must be seamless.

Device Management: Beyond just reading data, systems require a "Device Management" layer (like Adeunis' KARE+) to monitor battery levels and push firmware updates to the fleet remotely.

Scalability: This architecture allows for scaling from a single building to millions of housing units by decoupling the hardware layer from the application layer.

# IoT for Technical Performance

1. The Core Philosophy: Measurement-Driven Management

The fundamental principle of modern asset management is: "You cannot manage what you do not measure."

Traditional Management: Relies on scheduled maintenance (e.g., "Change filters every 6 months") or corrective maintenance (e.g., "Fix it because it's broken").

IoT-Driven Management: Relies on Condition-Based data. Maintenance is performed only when the data indicates a decline in performance.

2. Specialized IoT Sensor Deep-Dive

To optimize a building or factory, engineers deploy three primary "Sensor Families":

A. Differential Pressure (Delta P) Sensors

The Physics: Measures the difference in air pressure between two points (e.g., before and after a filter in a ventilation system).

Engineering Logic:

As a filter clogs with dust, the pressure difference (Delta P) increases.

The Alert: When Delta P hits a specific threshold, the system triggers a "Filter Replacement" task.

Value: Prevents motor strain (saving energy) and ensures air quality without wasting money on premature filter changes.

B. Dry Contact / State Sensors

Function 1 (State): Detects binary positions (Open/Closed, On/Off).

Function 2 (Counting): Tracks the number of "Events" or "Cycles."

Use Case (Elevators/Doors): By counting how many times an elevator door opens, engineers can predict when the mechanical rollers will fail based on manufacturer "Mean Time Between Failures" (MTBF) data.

C. Advanced Temperature Monitoring

Metrology: Using high-accuracy probes (ranging from -55°C to +155°C).

Health & Safety (Legionella): Monitoring the "Hot Water Loop." If water temperature drops below 50°C for too long, bacteria can grow. IoT provides 24/7 proof of compliance that manual checks cannot match.

3. The Maintenance Evolution

IoT transforms the workflow of the technical team:

Corrective: "The pump failed, everyone is angry, fix it now." (High cost, high stress).

Preventive: "Change the pump every 2 years regardless of condition." (High waste).

Predictive: "The vibration and temperature of the pump are rising; it will likely fail in 3 weeks. Schedule a replacement for next Tuesday." (Lowest cost, zero downtime).

4. Data Governance & Network Architecture

When scaling to thousands of units, the "Plumbing of Data" becomes critical.

Network Choice (LPWAN):

Private LoRaWAN: Preferred for high-density sites (like a campus or housing complex). It offers Zero Monthly Fees and total control over indoor coverage.

Public Cellular (NB-IoT/LTE-M): Preferred for scattered assets where installing a private gateway is not cost-effective.

Data Aggregation: A professional system must ingest data from three sources:

Direct IoT: Raw sensor data.

Third-Party: Data from service providers (e.g., the elevator company’s API).

Public/Utility: Smart meter data from the grid.

Security: Data must be hosted in high-security environments (Tier 4 Data Centers) and comply with GDPR (privacy) regulations.

5. Strategic Benefits Table

| Benefit | Engineering Mechanism | Business Outcome |
| --- | --- | --- |
| Energy Savings | Real-time anomaly detection in heating/cooling. | Lower utility bills. |
| Asset Longevity | Usage pattern analysis (avoiding over-use). | Extended equipment lifespan. |
| Operational Efficiency | Fewer "blind" technician inspections. | Reduced labor costs. |
| Tenant/User Comfort | Continuous IAQ (CO2/Temp) monitoring. | Higher satisfaction/productivity. |

Summary

Holistic View: Smart building management is not about a single sensor; it is about the Aggregation of heterogeneous data onto a single platform.

Sovereignty: By owning the IoT sensors, the building owner gains Data Sovereignty—they no longer rely solely on what the maintenance contractor tells them.

Scalability: Start with a "Pilot" (e.g., 40 units) to define the use cases, then standardize the "Hardware Stack" (Adeunis) and "Software Stack" for the full rollout.

# IoT Sensor Deployment & Installation

1. Network Architecture Selection

Before deployment, engineers must choose between two primary connectivity models:

Operated (Public) Networks:

Pros: Managed by a telecom provider; national/international coverage; no gateway maintenance.

Cons: Monthly subscription fees (OPEX); potential "white zones" (no coverage) in remote or underground areas.

Private Networks:

Pros: Full control over coverage; no monthly fees; data stays on local servers (security).

Cons: Initial hardware investment (CAPEX); requires internal expertise to maintain gateways.

2. The "Radio Mapping" Phase (Site Survey)

Installing sensors without a survey often leads to project failure.

Objective: Physically verify signal strength at every intended installation point.

Tool: A dedicated Field Test Device (FTD) or Network Tester.

Outcome:

Identify dead zones where a sensor will not be heard.

Optimize the placement of gateways (for private networks) or select the best operator (for public networks).

3. Physical Installation: The "Golden Rules"

To maximize radio propagation and battery life, follow these three engineering constraints:

Vertical Orientation: Antennas are designed to radiate horizontally. Sensors should always be mounted vertically.

Minimum Height (1.5 Meters): Installing sensors too close to the ground causes "Ground Reflection" which significantly weakens the signal.

Wall Offset (20 Centimeters): Do not mount a sensor flush against a concrete or metal wall. An offset of 20cm reduces signal attenuation and interference.

4. Environmental & Mechanical Constraints

Faraday Cages: Radio signals cannot escape fully enclosed metal cabinets.

Solution: Place the sensor outside the cabinet and run a probe/wire inside, or use an external antenna.

Extreme Temperatures:

Industrial Range: -20°C to +60°C.

Design Note: In refrigerated environments, the battery-powered sensor should be placed outside the fridge with a remote probe passed through the seal to preserve battery chemistry and signal strength.

Ingress Protection (IP Rating): Use IP67/68 enclosures for any environment with moisture, dust, or potential submersion.

Hazardous Zones (ATEX): In environments with explosive gases, sensors must be ATEX Certified (e.g., Zone 1) to ensure they cannot create a spark.

5. Configuration & Autonomy Balance

The "Return on Investment" (ROI) of an IoT project depends on battery life.

The Trade-off: High data granularity (sending data every minute) = Short battery life (months). Low data granularity (sending every hour) = Long battery life (10+ years).

Event-Driven Logic: Configure sensors to send a message immediately on an alarm (e.g., leak detected) but only periodically for heartbeat/status (e.g., once a day).

Tools: Use manufacturer-specific configuration apps (via USB, Bluetooth, or NFC) to batch-program devices before they reach the field.

6. Data Management & Decoding

The Payload: IoT sensors send compressed "Telegrams" (Hexadecimal) to save energy.

The Codec: A JavaScript or Python "Payload Decoder" is required at the server level to translate raw hex (e.g., 0x40...) into human-readable data (e.g., Temperature: 22°C).

Documentation: Always maintain a "Device Registry" linking the physical Serial Number (DevEUI) to its specific location and configured parameters.

Summary

Survey First: Never install a sensor without verifying the radio link with a tester.

Mount Correctly: 1.5m high, vertical, and away from walls.

Protect the Battery: Balance the transmission frequency against the required lifespan.

Standardize: Replicate configurations across the fleet to simplify long-term maintenance.

# IoT Transport Protocols

1. Wired Transport: Ethernet

The Gold Standard for Reliability: Uses physical RJ45 cables.

Pros: No interference, no passwords/pairing, extremely high speed (up to 1Gbps).

Power over Ethernet (PoE): A major advantage where the data cable also provides electricity to the device.

Cons: Not mobile. High power consumption (the Ethernet chip stays "hot" and draws 200-300mA constantly).

Best For: Fixed industrial machines, security cameras, and medical equipment.

2. High-Bandwidth Wireless: Wi-Fi

The Universal Standard: Available almost everywhere globally.

Pros: High data rates, low-cost modules, easy integration with existing IT infrastructure.

Cons: Power Hungry. Wi-Fi was designed for laptops, not tiny sensors. To save battery, you must use aggressive "sleep-and-wake" programming. It also suffers from 2.4GHz interference.

Best For: Indoor devices with access to power outlets or large batteries (Smart appliances, high-res sensors).

3. Short-Range Wireless: Bluetooth & BLE

Classic vs. Low Energy:

Classic: High speed, used for audio/voice.

BLE (Bluetooth Low Energy): Designed for tiny packets. Can run for a year on a coin-cell battery.

The Gateway Requirement: Bluetooth cannot talk to the internet directly. It needs a "bridge" (usually a smartphone or a dedicated BLE-to-Wi-Fi gateway).

Best For: Wearables, fitness trackers, and indoor "Beacons."

4. Long-Range Wireless: Cellular (4G/5G/LTE-M/NB-IoT)

The "Everywhere" Network: Uses existing cell towers.

Pros: Massive range, built-in security, and mobility (works on a moving truck).

Cons: High cost (monthly SIM fees). High power spikes (up to 2 Amps) when the radio transmits, which can crash weak batteries.

Best For: Fleet tracking, remote environmental monitoring, and off-grid infrastructure.

5. The IoT Specialists: LPWAN (LoRa & Sigfox)

These were invented specifically for the "Internet of Things."

LoRa (Long Range):

Uses unlicensed radio bands. You can build your own private network.

Range: Up to 15km+ rural.

Power: Extremely low.

Sigfox:

A managed "public" network. You pay a subscription per device.

Limit: Very small messages (12 bytes) and limited messages per day.

Best For: Agriculture, smart cities, and utility metering (water/gas).

6. Indoor Mesh: Zigbee & Z-Wave

The Mesh Concept: Instead of every device talking to one tower, they talk to each other. If Device A is too far from the hub, it sends its message to Device B, which passes it along.

Zigbee: Open standard, 2.4GHz.

Z-Wave: Proprietary, 900MHz (better penetration through walls).

Best For: Home/Building automation (lighting, thermostats).

📊 Engineering Trade-off Matrix

When choosing a protocol, you must balance three conflicting goals. You can usually only pick two:

| Protocol | Range | Power Life | Data Speed |
| --- | --- | --- | --- |
| Ethernet | Short (Cable) | Poor | Excellent |
| Wi-Fi | Short | Medium | Excellent |
| BLE | Very Short | Excellent | Medium |
| Cellular | Excellent | Poor | Excellent |
| LoRaWAN | Excellent | Excellent | Poor |
| Satellite | Infinite | Poor | Poor |

🏗️ Architectural Concept: The Gateway

Many IoT protocols (BLE, Zigbee, LoRa) are Non-IP. This means they don't speak the language of the internet (TCP/IP) directly.

The Edge Device: Uses a low-power radio (e.g., LoRa) to send a small packet.

The Gateway: A device with two radios. It hears the LoRa packet and "translates" it into an Ethernet or Wi-Fi packet to send to the Cloud.

Why do this? It allows the remote sensors to stay tiny and battery-efficient while the Gateway handles the "heavy lifting" of internet communication.

Teacher's Summary

If you have a plug: Use Ethernet or Wi-Fi.

If you have a battery and are close to a phone: Use BLE.

If you have a battery and are in the middle of nowhere: Use LoRa or NB-IoT.

If money is no object and you are in the ocean: Use Satellite.