Contents

- Relays in IoT Systems: EMR, SSR, and Safety

- Contactors vs Relays: Power Switching Fundamentals

- Relay Modules & Opto-Isolation

- Relays vs. Contactors

Use Ctrl + Click to open this Notion docs page

# Relays in IoT Systems: EMR, SSR, and Safety

1. What is a Relay? (The "Power Amplifier")

Definition: An electrically operated switch. It allows a Low Power Signal (like 5V from a microcontroller or IoT node) to control a High Power Circuit (like a 220V Pump or 24V Valve).

The Golden Rule: Galvanic Isolation. There is no electrical connection between the Low Voltage side (Primary) and the High Voltage side (Secondary). They are separated by magnetism or light.

Why this matters for Vaculink: If the 220V pump short circuits, the relay burns out, but your expensive IoT Gateway/Node remains safe.

2. The Two Main Technologies

A. Electromechanical Relay (EMR)

How it works: A coil creates a magnet

→

→

Pulls a metal arm (Armature)

→

→

Physical contacts touch ("Click").

Pros: Cheap, robust, true "Dry Contact" (0 leakage).

Cons: Slow, makes noise, mechanical parts wear out over time.

Use Case: Starting the big Vacuum Pumps.

B. Solid State Relay (SSR)

How it works: An LED inside shines light on a sensor

→

→

Semiconductor opens the gate. No moving parts.

Pros: Silent, incredibly fast, infinite lifespan (if not overheated), no sparks (safe for explosive sewer gas areas).

Cons: More expensive, generates heat, tiny "Leakage Current" (might confuse sensitive inputs).

Use Case: Fast switching logic, or hazardous environments (ATEX).

3. Relay Logic Types (Connecting to Fail-Safe Theory)

| Type | Behavior | Vaculink 3.0 Application |
| --- | --- | --- |
| Normally Open (NO) | OFF by default. Power coil to turn ON. | Warning Light: Only turn on when there is an alarm. |
| Normally Closed (NC) | ON by default. Power coil to turn OFF. | Safety Stop: If power fails, the relay closes and stops the machine. |
| Latching Relay | Stays in last position even if power is cut. | Memory: Remembering a state even if the IoT node battery dies. (Rarely used in critical safety). |

4. Poles and Throws (The Configurations)

Pole (P): How many separate circuits are being controlled?

Throw (T): How many positions can it connect to?

SPST (Single Pole Single Throw): Simple Light Switch. (On/Off).

SPDT (Single Pole Double Throw): The "Toggle" Switch.

Example: Common pin connects to Pump A (NC) OR Pump B (NO). It swaps between them.

DPST (Double Pole Single Throw): The "Safety" Switch.

Example: It cuts both the Live and Neutral wires of a 220V pump simultaneously for total isolation.

5. Critical Warning: Back EMF (The "Spike")

This is the #1 killer of IoT electronics.

The Phenomenon: When you turn OFF a relay coil, the magnetic field collapses instantly. This creates a massive reverse voltage spike (hundreds of volts) shooting back into your IoT device.

The Solution: Flyback Diode.

You must install a diode across the relay coil.

It acts as a "One-Way Valve" that circulates the spike back into the coil until it dies, protecting your Dragino/Adeunis device.

Note: Many industrial relay modules have this built-in, but raw relays do not.

🏗️ Analysis for Vaculink 3.0 System

1. Controlling the Vacuum Station (Remote Reset)

If you want to use the Dragino SN50v3 (which has a 5V output) or the Shelly to reboot a stuck PLC:

Wiring: Connect the Dragino 5V output to the Primary Coil of a Relay.

Secondary Side: Connect the Relay's NO (Normally Open) contacts to the PLC's "Reset" input.

Action: Dragino sends 5V

→

→

Relay Clicks (Closes)

→

→

PLC detects signal and reboots.

2. The "Wet" to "Dry" Converter

Sometimes you have a sensor that outputs 24V (Wet), but your Adeunis only accepts Dry Contacts.

Solution: Use an Interposing Relay.

Wiring: Sensor (24V) connects to Relay Coil. Relay Contacts (Dry) connect to Adeunis.

Result: The Relay converts the "Wet" 24V signal into a safe "Dry" click for the Adeunis.

Teacher's Summary

Relays are Isolators. They protect your smart brain (IoT) from the dumb muscle (Pumps).

Always check for Diodes. Never drive a raw relay coil directly from a microcontroller without protection.

SSR for Gas: If you are installing switching equipment inside a sewer pit (Methane risk), use Solid State Relays or Sealed Relays to avoid sparks.

You now understand the full chain:

Physical Event

→

→

Dry Contact Sensor

→

→

Adeunis Node

→

→

Gateway

→

→

Cloud

→

→

Dashboard

→

→

Human Decision

→

→

Relay

→

→

Pump Action.

# Contactors vs Relays: Power Switching Fundamentals

Contactors

1. What is a Contactor?

Definition: An electromechanical switch used to make or break the connection between a power supply and a high-power load (like an electric motor, heater, or lighting bank).

Primary Function: It allows a low-voltage control signal (e.g., 24V DC from a PLC) to safely switch a high-voltage power circuit (e.g., 400V AC).

Key Characteristic: Designed for high current and frequent switching, often with arc suppression features to handle the electrical sparks generated when disconnecting heavy loads.

2. Contactor vs. Relay: The Difference

While they operate on the same principle (magnetism closing a switch), they serve different roles:

| Feature | Relay | Contactor |
| --- | --- | --- |
| Current Capacity | Low (Typically < 10 Amps) | High (10 Amps to > 1000 Amps) |
| Primary Use | Control signals, logic, small electronics. | Switching main power to motors/loads. |
| Physical Size | Small, compact. | Large, robust, often noisy ("Clunk"). |
| Safety | Rarely has arc suppression. | Designed to extinguish electrical arcs. |

3. Anatomy & Wiring

A contactor has three distinct sections:

A. The Coil (Control Circuit)

Terminals: Usually marked A1 and A2.

Function: This is the electromagnet. When energized by the controller (PLC/BMS), it pulls the mechanical armature down.

Voltage: Must match the control system (e.g., 24V DC, 110V AC, 230V AC).

B. The Power Poles (Load Circuit)

Terminals: Inputs marked L1, L2, L3 (Line)

→

→

Outputs marked T1, T2, T3 (Terminal/Load).

Function: These carry the heavy current to the machine. They are Normally Open (NO), meaning they are disconnected when the coil is off.

3. The Auxiliary Contacts (Feedback Circuit)

Terminals: Often marked 13/14 (NO) or 21/22 (NC).

Function: Small, low-current contacts mechanically linked to the main power poles.

Purpose: To tell the control system the actual physical state of the contactor (Open or Closed).

4. Standard SCADA/PLC Logic Patterns

In professional automation, you never assume a machine is running just because you told it to. You use the Contactor's feedback to verify.

A. The "Run Status" Logic

Input: Read the Auxiliary Contact (NO) status.

Visualization:

If Aux Contact = Closed

→

→

Display "Motor Running" (Green).

If Aux Contact = Open

→

→

Display "Motor Stopped" (Grey/Red).

B. The "Fail to Start" Alarm (Discrepancy Alarm)

This detects if the contactor coil is broken or the control wire is cut.

Logic:

Controller sends Start Command (Output = True).

Wait Timer (e.g., 2 seconds) to allow mechanical movement.

Check Feedback Input.

IF Command == True AND Feedback == False:

TRIGGER ALARM: "Fail to Start."

C. The "Welded Contact" Alarm (Critical Safety)

This detects if the power poles have melted and fused together due to high current arcing, causing the motor to run uncontrollably.

Logic:

Controller sends Stop Command (Output = False).

Check Feedback Input.

IF Command == False AND Feedback == True:

TRIGGER ALARM: "Contactor Welded / Stuck On."

5. Component Hierarchy in Automation

Understanding where the contactor fits in the chain of command:

SCADA / HMI: The Supervisor. Displays status and issues high-level requests.

PLC / Controller: The Brain. Executes logic and sends voltage to the coil.

Interposing Relay (Optional): The Protector. Used if the PLC output cannot handle the current required by the Contactor coil.

Contactor: The Muscle. Physically connects the mains power.

Overload Relay: The Nerve. Sits after the contactor to detect if the motor is drawing too much current (thermal protection) and cuts the circuit if necessary.

# Relay Modules & Opto-Isolation

1. The Relay Module Architecture

In modern electronics prototyping and embedded systems, "Relay Modules" are preferred over raw component relays because they integrate essential driver and protection circuitry.

The Problem with Raw Relays: A standard microcontroller GPIO pin (e.g., 3.3V or 5V) typically outputs only 20mA–40mA. A relay coil often requires 70mA–100mA to energize. Connecting a coil directly to a microcontroller will likely burn out the pin.

The Module Solution: A relay module includes:

Transistor/MOSFET: Acts as an amplifier. The microcontroller sends a tiny signal to the transistor base, and the transistor switches the higher current for the coil.

Flyback Diode: A diode placed across the coil terminals. It absorbs the high-voltage "Back EMF" spike generated when the magnetic field collapses, preventing it from destroying the transistor or microcontroller.

Status LED: Provides immediate visual feedback on whether the logic signal is being received.

2. Opto-Isolation (Galvanic Isolation)

This is a critical safety feature found in higher-quality relay modules to separate the Low Voltage (Logic) side from the High Power (Coil/Load) side.

Mechanism: An Optocoupler (or Opto-isolator) is used. It contains an internal Infrared LED and a photosensor. The signal travels via light, not electricity.

The Benefit: Electrical noise, voltage spikes, or interference from the high-power load (like a motor or solenoid) cannot travel back through the wires to crash or damage the sensitive microcontroller.

Configuration (The JD-VCC Jumper):

Jumper ON (Shared Power): The relay coil is powered by the same source as the microcontroller. Isolation is bypassed.

Jumper OFF (Isolated Power): You provide a separate power supply to the JD-VCC pin for the coils. The microcontroller only powers the internal LED. This provides True Galvanic Isolation.

3. Signal Logic: Active High vs. Active Low

When integrating relays, it is vital to check the activation logic, as it varies by manufacturer.

Active High:

Input: Logic 1 (High Voltage / 5V).

Result: Relay Energizes (ON).

Common in: Solid State Relays and simple transistor circuits.

Active Low:

Input: Logic 0 (Ground / 0V).

Result: Relay Energizes (ON).

Common in: Multi-channel relay modules. This is often done to sink current into the microcontroller rather than source it, which is generally safer for the chip.

Implication: Your code must output LOW to turn the device ON, and HIGH to turn it OFF.

4. Motor Direction Control (H-Bridge Logic)

Relays can be arranged to reverse the polarity of a DC motor, allowing it to spin in both directions. This requires Two SPDT (Single Pole Double Throw) relays.

Wiring Configuration:

Motor Terminal A

→

→

Common (COM) of Relay 1.

Motor Terminal B

→

→

Common (COM) of Relay 2.

Normally Closed (NC) of both relays

→

→

Ground (GND).

Normally Open (NO) of both relays

→

→

Positive Voltage (V+).

Logic States:

Relay 1 ON, Relay 2 OFF: Terminal A is (+), Terminal B is (-). Motor spins Forward.

Relay 1 OFF, Relay 2 ON: Terminal A is (-), Terminal B is (+). Motor spins Reverse.

Both OFF: Both terminals are (-). Motor Brakes/Stops.

Both ON: Both terminals are (+). Motor Brakes/Stops.

Summary

Never drive a relay coil directly from a logic chip; always use a driver (transistor) and protection (diode).

Opto-isolation is the industry standard for protecting control logic from the noise of inductive loads (motors/coils).

Active Low logic is counter-intuitive (0 = ON) but very common; always verify the datasheet or test with a multimeter.

# Relays vs. Contactors

1. Fundamental Similarity

Operating Principle: Both devices are Electromagnetic Switches.

Mechanism: An electrical current energizes a coil, creating a magnetic field. This field physically pulls an armature to open or close electrical contacts.

Purpose: To control an electrical circuit automatically or remotely, replacing manual switches.

2. Key Differences: The "Scale" of Application

While they work the same way, they are designed for different load requirements.

| Feature | Relay | Contactor |
| --- | --- | --- |
| Primary Use | Control signals, Logic, Low Power loads. | High Power switching (Motors, Lighting Banks, Heaters). |
| Current Rating | Typically 5 to 15 Amps. | Typically 30 to 300+ Amps. |
| Physical Build | Small, compact components. | Large, robust, "beefy" components to handle heat and arcing. |
| Coil Type | Fixed. If the coil voltage is wrong, you replace the whole relay. | Modular. Coils are often replaceable (e.g., swap a 120V coil for a 277V coil). |
| Contact Logic | Usually provides both NO and NC contacts (Form C). | Usually Normally Open (NO) for power poles. |
| Latching | Rare. Usually requires continuous power to hold state. | Mechanical Latching available (stays ON even if power is lost). |

3. Detailed Component Analysis

A. Relays (The Logic Switch)

Contact Configuration: Relays are versatile. A single relay often allows you to switch one circuit ON while simultaneously switching another OFF (using the Common, NO, and NC terminals).

Load Capacity: Limited. They are not designed to handle the massive inrush current of a large motor starting up.

Maintenance: Generally considered disposable items. If they fail, the entire unit is replaced.

B. Contactors (The Power Switch)

Pole Capacity: Designed to control multiple high-voltage lines simultaneously.

Standard: 3-Poles (for 3-Phase Motors).

Lighting: Can control 4, 8, or even 12 separate lighting circuits in one unit.

Auxiliary Contacts: Since the main poles are usually just for power (NO), contactors often use add-on "Auxiliary Blocks" to provide low-current feedback signals (NO/NC) to control systems.

Mechanical Latching: A feature specific to contactors (often used in lighting). A mechanical mechanism holds the contactor closed so the coil does not need to stay energized, saving energy and keeping lights on during momentary power control glitches.

4. Selection Criteria

When designing a panel, choose based on the load:

Select a Relay if:

The current is low (< 10-15 Amps).

You need complex logic (switching between NO and NC).

Space in the panel is limited.

You are switching control signals (e.g., telling a PLC input to turn on).

Select a Contactor if:

The load is high current (Motors, large heating elements).

The voltage is high (480V, etc.).

You need to switch many poles (3-Phase or multi-circuit lighting).

You need the device to be repairable (changing coils/contacts) rather than disposable.

Summary

Relays are for Brains (Control Logic and small loads).

Contactors are for Muscles (Heavy lifting and high power).

Always check the Amperage Rating and Coil Voltage before selection.